## Taul1
Modbus Registers |  | Windis Free & Windis Ceil |  | Software version: | 2025-01-26
Input Registers | Register | Name |  | Device Type | Scale | Offset | Unit | Description
| 30001 | Air temp in |  | Signed 16-bit | 10 | 0 | °C | Inlet air tempereture
| 30002 | Air temp out |  | Signed 16-bit | 10 | 0 | °C | Outlet air temperature
| 30003 | Indoor temp |  | Signed 16-bit | 10 | 0 | °C | Room temperature
| 30004 | Outdoor temp |  | Signed 16-bit | 10 | 0 | °C | Outdoor temperature
| 30005 | TOh Outdoor |  | Signed 16-bit | 10 | 0 | %RH | Outdoor Humidity
| 30006 | Water temp in |  | Signed 16-bit | 10 | 0 | °C | Inlet water temperature
| 30007 | Water temp out |  | Signed 16-bit | 10 | 0 | °C | Outlet water temperature
| 30008 | Water temp Delta |  | Signed 16-bit |  | 0 | °C | Water temperature difference
| 30009 | Flow [l/s] |  | Signed 16-bit | 1000 | 0 | l/s | Water flow
| 30010 | Power [kW] |  | Signed 16-bit | 10 | 0 | kW | Unit heating capacity
| 30011 | Airbubble detection level 0 = No air, 1 = small amount of air, 2 = medium amount of air, 3 = high amount of air, 4 = completely in air |  | Unsigned 16-bit |  |  | - | Airbubble detection level 0 = No air, 1 = small amount of air, 2 = medium amount of air, 3 = high amount of air, 4 = completely in air
| 30012 | Cumulative heating energy [kWh] x10 |  | Unsigned 32-bit | 10 |  | kWh | Cumulative heating energy [kWh] x10
| 30013 | Cumulative heating energy [kWh] x10 HiR | [5 empty] | Cumulative heating energy [kWh] x10 HiR
| 30014 | TODO: Air filter pressure difference [Pa] |  | Unisgned 16-bit | 1 |  | Pa | TODO: Air filter pressure difference [Pa]
| 30015 | Fan speed [%] |  | Unisgned 16-bit | 1 |  | % | Fan speed [%]
| 30016 | Heating valve position [%] |  | Unisgned 16-bit | 1 |  | % | Heating valve position [%]
| 30017 | Status registers [table 1] |  | Unisgned 16-bit |  |  |  | Status registers [table 1]
| 30018 | Alarm registers [table 2] |  | Unisgned 16-bit |  |  |  | Alarm registers [table 2]
| 30019 | Active alarms count |  | Unisgned 16-bit | 1 |  | Qty | Active alarms count
| 30020 | Pressure |  | Signed 16-bit | 10 |  | bar | Water System Pressure
Slave 1 Input registers
| 30101 | Air temp in x10 |  | Signed 16-bit | 10 | 0 | °C | Inlet air tempereture
| 30102 | Air temp out x10 |  | Signed 16-bit | 10 | 0 | °C | Outlet air temperature
| 30103 | Indoor temp x10 |  | Signed 16-bit | 10 | 0 | °C | Room temperature
| 30104 | Outdoor temp x10 |  | Signed 16-bit | 10 | 0 | °C | Outdoor temperature
| 30105 | TOh Outdoor Humidity(option) [%RH] |  | Signed 16-bit | 10 | 0 | %RH | Outdoor Humidity
| 30106 | Water temp in x10 |  | Signed 16-bit | 10 | 0 | °C | Inlet water temperature
| 30107 | Water temp out x10 |  | Signed 16-bit | 10 | 0 | °C | Outlet water temperature
| 30108 | Water temp deltaT x10 |  | Signed 16-bit |  | 0 | °C | Water temperature difference
| 30109 | Flow [l/s]x1000 |  | Signed 16-bit | 1000 | 0 | l/s | Water flow
| 30110 | Power [kW] x10 |  | Signed 16-bit | 10 | 0 | kW | Unit heating capacity
| 30111 | Airbubble detection level 0 = No air, 1 = small amount of air, 2 = medium amount of air, 3 = high amount of air, 4 = completely in air |  | Unsigned 16-bit |  |  | - | Airbubble detection level 0 = No air, 1 = small amount of air, 2 = medium amount of air, 3 = high amount of air, 4 = completely in air
| 30112 | Cumulative heating energy [kWh] x10 LoR |  | Unsigned 32-bit | 10 |  | kWh | Cumulative heating energy [kWh] x10
| 30113 | Cumulative heating energy [kWh] x10 HiR | [5 empty] | Cumulative heating energy [kWh] x10 HiR
| 30114 | TODO: Air filter pressure difference [Pa] |  | Unisgned 16-bit | 1 |  | Pa | TODO: Air filter pressure difference [Pa]
| 30115 | Fan speed [%] |  | Unisgned 16-bit | 1 |  | % | Fan speed [%]
| 30116 | Heating valve position [%] |  | Unisgned 16-bit | 1 |  | % | Heating valve position [%]
| 30117 | Status registers [table 1] |  | Unisgned 16-bit |  |  |  | Status registers [table 1]
| 30118 | Alarm registers [table 2] |  | Unisgned 16-bit |  |  |  | Alarm registers [table 2]
| 30119 | Active alarms count |  | Unisgned 16-bit | 1 |  | Qty | Active alarms count
| 30120 | Pressure |  | Signed 16-bit | 10 |  | bar | Water System Pressure
Slave 2 Input registers
| 30201 | Air temp in x10 |  | Signed 16-bit | 10 | 0 | °C | Inlet air tempereture
| 30202 | Air temp out x10 |  | Signed 16-bit | 10 | 0 | °C | Outlet air temperature
| 30203 | Indoor temp x10 |  | Signed 16-bit | 10 | 0 | °C | Room temperature
| 30204 | Outdoor temp x10 |  | Signed 16-bit | 10 | 0 | °C | Outdoor temperature
| 30205 | TOh Outdoor Humidity(option) [%RH] |  | Signed 16-bit | 10 | 0 | %RH | Outdoor Humidity
| 30206 | Water temp in x10 |  | Signed 16-bit | 10 | 0 | °C | Inlet water temperature
| 30207 | Water temp out x10 |  | Signed 16-bit | 10 | 0 | °C | Outlet water temperature
| 30208 | Water temp deltaT x10 |  | Signed 16-bit |  | 0 | °C | Water temperature difference
| 30209 | Flow [l/s]x1000 |  | Signed 16-bit | 1000 | 0 | l/s | Water flow
| 30210 | Power [kW] x10 |  | Signed 16-bit | 10 | 0 | kW | Unit heating capacity
| 30211 | Airbubble detection level 0 = No air, 1 = small amount of air, 2 = medium amount of air, 3 = high amount of air, 4 = completely in air |  | Unsigned 16-bit |  |  | - | Airbubble detection level 0 = No air, 1 = small amount of air, 2 = medium amount of air, 3 = high amount of air, 4 = completely in air
| 30212 | Cumulative heating energy [kWh] x10 LoR |  | Unsigned 32-bit | 10 |  | kWh | Cumulative heating energy [kWh] x10
| 30213 | Cumulative heating energy [kWh] x10 HiR | [5 empty] | Cumulative heating energy [kWh] x10 HiR
| 30214 | TODO: Air filter pressure difference [Pa] |  | Unisgned 16-bit | 1 |  | Pa | TODO: Air filter pressure difference [Pa]
| 30215 | Fan speed [%] |  | Unisgned 16-bit | 1 |  | % | Fan speed [%]
| 30216 | Heating valve position [%] |  | Unisgned 16-bit | 1 |  | % | Heating valve position [%]
| 30217 | Status registers [table 1] |  | Unisgned 16-bit |  |  |  | Status registers [table 1]
| 30218 | Alarm registers [table 2] |  | Unisgned 16-bit |  |  |  | Alarm registers [table 2]
| 30219 | Active alarms count |  | Unisgned 16-bit | 1 |  | Qty | Active alarms count
| 30220 | Pressure |  | Signed 16-bit | 10 |  | bar | Water System Pressure
Slave 3 Input registers
| 30301 | Air temp in x10 |  | Signed 16-bit | 10 | 0 | °C | Inlet air tempereture
| 30302 | Air temp out x10 |  | Signed 16-bit | 10 | 0 | °C | Outlet air temperature
| 30303 | Indoor temp x10 |  | Signed 16-bit | 10 | 0 | °C | Room temperature
| 30304 | Outdoor temp x10 |  | Signed 16-bit | 10 | 0 | °C | Outdoor temperature
| 30305 | TOh Outdoor Humidity(option) [%RH] |  | Signed 16-bit | 10 | 0 | %RH | Outdoor Humidity
| 30306 | Water temp in x10 |  | Signed 16-bit | 10 | 0 | °C | Inlet water temperature
| 30307 | Water temp out x10 |  | Signed 16-bit | 10 | 0 | °C | Outlet water temperature
| 30308 | Water temp deltaT x10 |  | Signed 16-bit |  | 0 | °C | Water temperature difference
| 30309 | Flow [l/s]x1000 |  | Signed 16-bit | 1000 | 0 | l/s | Water flow
| 30310 | Power [kW] x10 |  | Signed 16-bit | 10 | 0 | kW | Unit heating capacity
| 30311 | Airbubble detection level 0 = No air, 1 = small amount of air, 2 = medium amount of air, 3 = high amount of air, 4 = completely in air |  | Unsigned 16-bit |  |  | - | Airbubble detection level 0 = No air, 1 = small amount of air, 2 = medium amount of air, 3 = high amount of air, 4 = completely in air
| 30312 | Cumulative heating energy [kWh] x10 LoR |  | Unsigned 32-bit | 10 |  | kWh | Cumulative heating energy [kWh] x10
| 30313 | Cumulative heating energy [kWh] x10 HiR | [5 empty] | Cumulative heating energy [kWh] x10 HiR
| 30314 | TODO: Air filter pressure difference [Pa] |  | Unisgned 16-bit | 1 |  | Pa | TODO: Air filter pressure difference [Pa]
| 30315 | Fan speed [%] |  | Unisgned 16-bit | 1 |  | % | Fan speed [%]
| 30316 | Heating valve position [%] |  | Unisgned 16-bit | 1 |  | % | Heating valve position [%]
| 30317 | Status registers [table 1] |  | Unisgned 16-bit |  |  |  | Status registers [table 1]
| 30318 | Alarm registers [table 2] |  | Unisgned 16-bit |  |  |  | Alarm registers [table 2]
| 30319 | Active alarms count |  | Unisgned 16-bit | 1 |  | Qty | Active alarms count
| 30320 | Pressure |  | Signed 16-bit | 10 |  | bar | Water System Pressure
Holding Registers
| 40001 | Indoor_T from BMS x10 |  | Signed 16-bit | 10 | 0 | °C | Indoor temp from BMS
| 40002 | Indoor_T selector 0 = IO, 1= COM, 5= auto |  | Unsigned 16-bit | 10 | 0 | °C | sensor value selector
| 40003 | TOa from BMS |  | Signed 16-bit | 10 | 0 | °C | Outdoor temp from BMS
| 40004 | TOa selector 0 = IO, 1= COM |  | Unsigned 16-bit | 10 | 0 | °C | sensor value selector
| 40005 | EnableUnit from BMS |  | Unsigned 16-bit |  |  |  | Enable Unit from BMS
| 40006 | EnableUnit selector 0 = IO, 1= COM |  | Unsigned 16-bit |  |  |  | IO value selector
| 40007 | DoorSwitch from BMS |  | Unsigned 16-bit |  |  |  | Doorswitch from BMS
| 40008 | DoorSwitch selector 0 = IO, 1= COM |  | Unsigned 16-bit |  |  |  | IO value selector
| 40009 | Day/Night status 0=Night, 1=Day |  | Unsigned 16-bit |  |  |  | Day switch from BMS
| 40010 | DayNight selector 0 = IO, 1= COM |  | Unsigned 16-bit |  |  |  | IO value selector
| 40011 | Room SP day x10 |  | Unsigned 16-bit | 10 | 0 | °C | Room setpoint in Day state
| 40012 | Room hysteresis |  | Unsigned 16-bit | 10 | 0 | K | Room setpoint hysterestis
| 40013 | Room SP night x10 |  | Unsigned 16-bit | 10 | 0 | °C | Room setpoint in Night state
| 40014 | PostRun delay |  | Unsigned 16-bit | 1 | 0 | s | Fan post run delay
| 40015 | AlmAck |  | Unsigned 16-bit |  |  |  | Write 1 to Acknowledge all alarms
| 40016 | Installation Hei |  | Unsigned 16-bit | 1 | 0 | cm | Installation Height
| 40017 | Fan Speed max60 |  | Unsigned 16-bit | 1 | 0 | % | Fan Speed max @ installation height 200cm
| 40018 | Fan Speed max70 |  | Unsigned 16-bit | 1 | 0 | % | Fan Speed max @ installation height 250cm
| 40019 | Fan Speed max80 |  | Unsigned 16-bit | 1 | 0 | % | Fan Speed max @ installation height 300cm
| 40020 | Fan Speed max90 |  | Unsigned 16-bit | 1 | 0 | % | Fan Speed max @ installation height 350cm
| 40021 | Fan Speed max @ installation height 400cm |  | Unsigned 16-bit | 1 | 0 | % | Fan Speed max @ installation height 400cm
| 40022 | Speed at -20°C |  | Signed 16-bit | 1 | 0 | % | Speed at -20°C
| 40023 | Speed at -10°C |  | Signed 16-bit | 1 | 0 | % | Speed at -10°C
| 40024 | Speed at -5°C |  | Signed 16-bit | 1 | 0 | % | Speed at -5°C
| 40025 | Speed at -0°C |  | Signed 16-bit | 1 | 0 | % | Speed at -0°C
| 40026 | Speed at 5°C |  | Signed 16-bit | 1 | 0 | % | Speed at 5°C
| 40027 | Speed at 15°C |  | Signed 16-bit | 1 | 0 | % | Speed at 15°C
| 40028 | Speed at 20°C |  | Signed 16-bit | 1 | 0 | % | Speed at 20°C
| 40029 | Speed at 30°C |  | Signed 16-bit | 1 | 0 | % | Speed at 30°C
| 40030 | BMS Manual control (registers H31-32) 0 = auto, 1 = manual |  | Unsigned 16-bit |  |  | - | Set to 1 to enable following registers
| 40031 | Manual Fan Speed (0-100%) from BMS |  | Unsigned 16-bit | 1 | 0 | % | Manual fanspeed from BMS
| 40032 | Manual Heating valve position (0-100%) from BMS |  | Unsigned 16-bit | 1 | 0 | % | Manual heating valve position
| 40022 | Temp.supply at -20°C |  | Signed 16-bit | 1 | 0 | °C | Temp.supply at -20°C
| 40023 | Temp.supply at -10°C |  | Signed 16-bit | 1 | 0 | °C | Temp.supply at -10°C
| 40024 | Temp.supply att -5°C |  | Signed 16-bit | 1 | 0 | °C | Temp.supply att -5°C
| 40025 | Temp.supply at -0°C |  | Signed 16-bit | 1 | 0 | °C | Temp.supply at -0°C
| 40026 | Temp.supply att 5°C |  | Signed 16-bit | 1 | 0 | °C | Temp.supply att 5°C
| 40027 | Temp.supply at 15°C |  | Signed 16-bit | 1 | 0 | °C | Temp.supply at 15°C
| 40028 | Temp.supply at 20°C |  | Signed 16-bit | 1 | 0 | °C | Temp.supply at 20°C
| 40029 | Temp.supply at 30°C |  | Signed 16-bit | 1 | 0 | °C | Temp.supply at 30°C
table 1
Status: bit1 |  | 0x2204 'AirCurtain\DoorSwitch' 0x810A |  | Input 17 | Unsigned Integer
Status: bit2 |  | 0x2204 'AirCurtain\Enable_Disable' 0x810A
Status: bit3 |  | 0x2204 'AirCurtain\Day_Night' 0x810A
|  | 0x2204 'AirCurtain\DoorSwitch' 0x810A | <0x0100,-1,I9,0,rw,1> |  |  |  |  | Door Switch status
|  | 0x2204 'AirCurtain\Enable_Disable' 0x810A | <0x0100,-1,I10,0,rw,1> |  |  |  |  | Enable status
|  | 0x2204 'AirCurtain\Day_Night' 0x810A | <0x0100,-1,I11,0,rw,1> |  |  |  |  | Day/Night Status
table 2
Alarm: bit1 |  | AirIn_T sensor fault |  | Input18 | Unsigned Integer |  |  | AirIn_T sensor fault
Alarm: bit2 |  | AirOut_T sensor fault | [5 empty] | AirOut_T sensor fault
Alarm: bit3 |  | IndoorT sensor fault | [5 empty] | IndoorT sensor fault
Alarm: bit4 |  | Toa/TOh sensor/communication fault | [5 empty] | Toa/TOh sensor/communication fault
Alarm: bit5 |  | WaterIn_T sensor fault | [5 empty] | WaterIn_T sensor fault
Alarm: bit6 |  | WaterOut_T sensor fault | [5 empty] | WaterOut_T sensor fault
Alarm: bit7 |  | Air Bubble alarm | [5 empty] | Air Bubble alarm
Alarm: bit8 |  | Freeze protection | [5 empty] | Freeze protection
Alarm: bit9 |  | Fan feedback alarm | [5 empty] | Fan feedback alarm
Alarm: bit10 |  | dP Filter alarm | [5 empty] | dP Filter alarm
Alarm: bit11 |  | Communication alarm Flow sensor | [5 empty] | Communication alarm Flow sensor
Alarm: bit12 |  | Communication alarm Slave 1 | [5 empty] | Communication alarm Slave 1
Alarm: bit13 |  | Communication alarm Slave 2 | [5 empty] | Communication alarm Slave 2
Alarm: bit14 |  | Communication alarm Slave 3 | [5 empty] | Communication alarm Slave 3
Alarm: bit15 |  | Sum alarm from slaves (any alarm in any slave) | [5 empty] | Sum alarm from slaves (any alarm in any slave)
Alarm: bit16 |  | Filter dirty | [5 empty] | Filter dirty